## Slide 1: Smoke transport modeling: detection system design
9th Triennial International Aircraft Fire and Cabin Safety Research Conference
October 28-31, 2019
Atlantic City, New Jersey, USA
Changmin Cao, Kalyan Gottiparthi, Jordan Snyder, Jason Wegge, Vaidya Sankaran, May Corn
United Technologies Research Center
Amanda Daly, Kenneth Bell, Terry Simpson, Eli Baldwin
Kidde Fire Protection Systems

## Slide 2: Detection system design tool development
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
augment and streamline detection system certification process
Benefits:
Virtual tests
Parametric variations
Physical insight
Accelerate design & development
Provide confidence in detection system layout
Reduce number of flight certification tests
Reduce cost of certification
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 3: Model Development approach
Modeling approach validated to date:
Smoke generator input conditions
Buoyant plume
Ceiling jet flow
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Validate models in a
laboratory setting
(2) Apply validated models
to the cargo bay
Additional models to validate:
Smoke arrival time
Detector response time
Pre-Test Prediction of System Response in Cargo Bay
Today’s Presentation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 4: alarm time measurements: UTRC Lab
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
1
2
3
Smoke arrival time
Determined from the time lag between obscuration beam measurements &
1
2
Detector response time
Determined from the obscuration beam measurement and the time when detector alarms
2
3
Detector
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 5: CFD model set-Up: UTRC LAb
3-D, unsteady solver from NIST (version 6.6.0) Large Eddy Simulation (LES)
Fire Dynamics Simulator (FDS)
Numerical simulation using a non-uniform sized mesh
Input conditions: measured at smoke generator exit plane
Detector response model: calibrated to detector
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 6: Validation of smoke transport & detector response models with lab data
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Detector response time
Smoke arrival time
Time to alarm (sec)
Simulation predicts within 2-3 seconds of measured data
Next step: Apply modeling approach to the cargo bay
Low smoke mass flow
Low ceiling
Mid smoke mass flow
Low ceiling
Model Exp. Data
Model Exp. Data
High smoke mass flow
High ceiling
Model Exp. Data
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 7: CFD model set-Up: cargo bay
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Simulation using Non-uniform sized mesh
Utilized same smoke generator input conditions and calibrated detector response model used in UTRC lab simulation
3-D, unsteady solver from NIST (version 6.6.0) Large Eddy Simulation (LES)
Fire Dynamics Simulator (FDS)
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 8: Simulation matrix variables
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Ventilation Schedule
Outlet vent
Inlet vent
Smoke Generator Positions
SG5
Inlet vent
Outlet vent
Door
SG4
SG3
SG2
SG1
Obstruction location
Obstruction
D4
D3
D2
D1
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 9: smoke transport & alarm time: empty cargo bay
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
D4
D3
D2
D1
1.0
0.0
Smoke mass fraction
- Smoke generator located toward one end of the cargo bay
- No ventilation
SG5
Simulated smoke propagation
Alarm time for each detector from simulation
from simulation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 10: smoke transport & alarm time: empty cargo bay
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
D4
D3
D2
D1
SG3
1.0
0.0
Smoke mass fraction
- Smoke generator located in the center of the cargo bay
- No ventilation
SG3
Simulated smoke propagation
Alarm time for each detector from simulation
from simulation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 11: smoke transport & alarm time: empty cargo bay
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Simulations predict expected trends in detector alarm time
SG5
SG4
SG3
SG2
SG1
D4
D3
D2
D1
SG1
SG3
SG5
Alarm time for each detector from simulations
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 12: empty cargo bay — Effect of ventilation
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
inlet air initially pushes against smoke transported across ceiling
No ventilation
With ventilation
Inlet vent
Outlet vent
SG3
SG3
Simulated smoke propagation
Simulated smoke propagation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 13: empty cargo bay — Effect of ventilation
No ventilation
With ventilation
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
1.0
0.0
Smoke mass fraction
D4
D3
D2
D1
inlet air initially pushes against smoke transported across ceiling
SG3
SG3
from simulation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 14: empty cargo bay — Effect of ventilation
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Ventilation effect on smoke transport depends on smoke generator position
SG5
SG4
SG3
SG2
SG1
D4
D3
D2
D1
SG3 With ventilation schedule
SG3
Inlet vent
Outlet vent
SG5 with ventilation schedule
SG5
Alarm time for each detector from simulations
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 15: Analysis of empty cargo bay results
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Alarm times versus distance between smoke generator and detector
Empty cargo bay
Empty cargo bay with ventilation schedule
Ventilation introduces additional flow field dynamics that cause non-linear deviations
Detection time > 60 sec
Alarm time for each detector from simulations
Alarm time for each detector from simulations
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 16: Ventilated Cargo bay with obstruction
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
D4
D3
D2
D1
SG5
SG5
- Smoke generator located toward one end of the cargo bay
Inlet vent
Outlet vent
SG5 with ventilation schedule
SG5 + ventilation schedule + obstruction
1.0
0.0
Smoke mass fraction
Simulated smoke propagation
Alarm time for each detector from simulation
from simulation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 17: Ventilated Cargo bay with obstruction
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
D4
D3
D2
D1
SG3
SG3
- Smoke generator located in the center of the cargo bay
Inlet vent
Outlet vent
1.0
0.0
Smoke mass fraction
SG3 with ventilation schedule
SG3 + ventilation schedule + obstruction
Simulated smoke propagation
Alarm time for each detector from simulation
from simulation
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 18: Analysis of cases with obstruction
Obstruction can additionally affect smoke transport and subsequently the detector alarm time
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Ventilated cargo bay with obstruction
Alarm times versus distance between smoke generator and detector
Ventilated cargo bay, no obstruction
Detection times > 60 sec
Detection time > 60 sec
Alarm time for each detector from simulations
Alarm time for each detector from simulations
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 19: Detection system performance evaluation
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Predicted system times based on when two detectors alarm
12 cases simulated:
Varied smoke generator positions
Effect of ventilation schedule
Effect of obstruction
In this particular configuration, the presence of an obstruction is predicted to increase the system alarm time by ~35%
No ventilation
With ventilation
With ventilation
With obstruction
No ventilation
With obstruction
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.

## Slide 20: Summary and Next steps
9th Triennial International Aircraft Fire and Cabin Safety Research Conference, October 28-31, 2019, Atlantic City, New Jersey, USA
Next step
Collect data in the cargo bay test facility to validate these simulations and mature tool
Additional models validated
Smoke arrival time
Detector response time
In this specific modeled cargo bay configuration
Ventilation location and schedule impacts smoke transport
Obstructions produce a significant effect on smoke transport
© 2019 Collins Aerospace, a United Technologies company. All rights reserved.